|  |  |  |  |
| --- | --- | --- | --- |
|  |  |  |  |
|  | |

**CALIBRATION CERTIFICATE**

|  |  |  |
| --- | --- | --- |
| **CUSTOMER NAME & ADDRESS:**  **M/s. Glenmark Pharmaceuticals Ltd.**  Plot No:-E37 To E39, D Road, MIDC Satpur, Nashik,  Maharashtra- 422007 |  |  |
|  |  |
|  |  |
|  |  |
| **INSTRUMENT DESCRIPTION**  Make : Protech Dew point Monitor(Supply Air)  Model : DPHT-3  SI. No : BAS-H2DF-30  Range : 0 to 100° C &30- 90RH%  AHU No : 36 |  |  |
| **Reference No** | PRT:9144/2021-2022 |
| **Date of Calibration** | 13.09.2021 |
| **Recommended Due Date** | 12.09.2022 |
| **Environmental condition** | Temperature : 0 -100 0 C |
| Relative Humidity : 30-90% |
| **Instrument Condition** | Good |

|  |  |
| --- | --- |
| **Standard / Calibration Used** | **Traceable to** |
| TESTO 625 Thermo hygrometer  Sl.No:62936315 | Trace able to National Standards  Cert No: 012101349  Due Date: 02.08.2022 |

The Calibration used is traceable to national standards

**CALIBRATION RESULTS**

**TEMPERATURE (°C)**

|  |  |  |  |  |
| --- | --- | --- | --- | --- |
| **SL.No** | **Standard Readings** | **UUC Readings** | **Deviation** | **Max Error** |
| 1 | 05.2 | 05.1 | -0.1 | ±0.3°C |
| 2 | 15.1 | 14.9 | -0.2 | ±0.3°C |
| 3 | 25.3 | 25.5 | +0.2 | ±0.3°C |
| 4 | 47.2 | 46.9 | -0.3 | ±0.3°C |
| 5 | 55.2 | 55.3 | +0.1 | ±0.3°C |

**HUMIDITY (RH %)**

|  |  |  |  |  |
| --- | --- | --- | --- | --- |
| **Sl.No** | **Standard Readings** | **UUC Readings** | **Deviations** | **Max Error** |
| 1 | 95 | 94 | -1 | ±5% |
| 2 | 73 | 75 | +2 | ±5% |
| 3 | 63 | 58 | -5 | ±5% |
| 4 | 43 | 39 | -4 | ±5% |
| 5 | 33 | 30 | -3 | ±5% |

**Remarks**: *All Parameters are well within the acceptable*

Calibrated by

Date: 13.09.2021

|  |  |  |  |
| --- | --- | --- | --- |
|  |  |  |  |
|  | |

**CALIBRATION CERTIFICATE**

|  |  |  |
| --- | --- | --- |
| **CUSTOMER NAME & ADDRESS:**  **M/s. Glenmark Pharmaceuticals Ltd.**  Plot No:-E37 To E39, D Road, MIDC Satpur, Nashik,  Maharashtra- 422007 |  |  |
|  |  |
|  |  |
|  |  |
| **INSTRUMENT DESCRIPTION**  Make : Protech Dew point Monitor(Return Air)  Model : DPHT-3  SI. No : BAS-H2DF-30  Range : 0 to 100° C &30- 90RH%  AHU No : 36 |  |  |
| **Reference No** | PRT:9145/2021-2022 |
| **Date of Calibration** | 13.09.2021 |
| **Recommended Due Date** | 12.09.2022 |
| **Environmental condition** | Temperature : 0 -100 0 C |
| Relative Humidity : 30-90% |
| **Instrument Condition** | Good |

|  |  |
| --- | --- |
| **Standard / Calibration Used** | **Traceable to** |
| TESTO 625 Thermo hygrometer  Sl.No:62936315 | Trace able to National Standards  Cert No: 012101349  Due Date: 02.08.2022 |

The Calibration used is traceable to national standards

**CALIBRATION RESULTS**

**TEMPERATURE (°C)**

|  |  |  |  |  |
| --- | --- | --- | --- | --- |
| **SL.No** | **Standard Readings** | **UUC Readings** | **Deviation** | **Max Error** |
| 1 | 05.2 | 05.0 | -0.2 | ±0.3°C |
| 2 | 15.1 | 14.8 | -0.3 | ±0.3°C |
| 3 | 25.3 | 25.4 | +0.1 | ±0.3°C |
| 4 | 47.2 | 47.0 | -0.2 | ±0.3°C |
| 5 | 55.2 | 55.5 | +0.3 | ±0.3°C |

**HUMIDITY (RH %)**

|  |  |  |  |  |
| --- | --- | --- | --- | --- |
| **Sl.No** | **Standard Readings** | **UUC Readings** | **Deviations** | **Max Error** |
| 1 | 95 | 90 | -5 | ±5% |
| 2 | 73 | 76 | +3 | ±5% |
| 3 | 63 | 62 | -1 | ±5% |
| 4 | 43 | 45 | +2 | ±5% |
| 5 | 33 | 29 | -4 | ±5% |

**Remarks**: *All Parameters are well within the acceptable*

Calibrated by

Date: 13.09.2021

|  |  |  |  |
| --- | --- | --- | --- |
|  |  |  |  |
|  | |

**CALIBRATION CERTIFICATE**

|  |  |  |
| --- | --- | --- |
| **CUSTOMER NAME & ADDRESS:**  **M/s. Glenmark Pharmaceuticals Ltd.**  Plot No:-E37 To E39, D Road, MIDC Satpur, Nashik,  Maharashtra- 422007 |  |  |
|  |  |
|  |  |
|  |  |
| **INSTRUMENT DESCRIPTION**  Make : Protech Dew point Monitor(Fresh Air)  Model : DPHT-3  SI. No : BAS-H2DF-30  Range : 0 to 100° C &30- 90RH%  AHU No : 36 |  |  |
| **Reference No** | PRT:9146/2021-2022 |
| **Date of Calibration** | 13.09.2021 |
| **Recommended Due Date** | 12.09.2022 |
| **Environmental condition** | Temperature : 0 -100 0 C |
| Relative Humidity : 30-90% |
| **Instrument Condition** | Good |

|  |  |
| --- | --- |
| **Standard / Calibration Used** | **Traceable to** |
| TESTO 625 Thermo hygrometer  Sl.No:62936315 | Trace able to National Standards  Cert No: 012101349  Due Date: 02.08.2022 |

The Calibration used is traceable to national standards

**CALIBRATION RESULTS**

**TEMPERATURE (°C)**

|  |  |  |  |  |
| --- | --- | --- | --- | --- |
| **SL.No** | **Standard Readings** | **UUC Readings** | **Deviation** | **Max Error** |
| 1 | 05.2 | 05.1 | -0.1 | ±0.3°C |
| 2 | 15.1 | 15.3 | +0.2 | ±0.3°C |
| 3 | 25.3 | 25.5 | +0.2 | ±0.3°C |
| 4 | 47.2 | 48.9 | -0.3 | ±0.3°C |
| 5 | 55.2 | 55.0 | -0.2 | ±0.3°C |

**HUMIDITY (RH %)**

|  |  |  |  |  |
| --- | --- | --- | --- | --- |
| **Sl.No** | **Standard Readings** | **UUC Readings** | **Deviations** | **Max Error** |
| 1 | 95 | 92 | -3 | ±5% |
| 2 | 73 | 75 | +2 | ±5% |
| 3 | 63 | 59 | -4 | ±5% |
| 4 | 43 | 42 | -1 | ±5% |
| 5 | 33 | 30 | -3 | ±5% |

**Remarks**: *All Parameters are well within the acceptable*

Calibrated by

Date: 13.09.2021

|  |  |  |  |
| --- | --- | --- | --- |
|  |  |  |  |
|  | |

**CALIBRATION CERTIFICATE**

|  |  |  |
| --- | --- | --- |
| **CUSTOMER NAME & ADDRESS:**  **M/s. Glenmark Pharmaceuticals Ltd.**  Plot No:-E37 To E39, D Road, MIDC Satpur, Nashik,  Maharashtra- 422007 |  |  |
|  |  |
|  |  |
|  |  |
| **INSTRUMENT DESCRIPTION**  Make : Protech Temperature Sensor  Model : AX-3(Supply Air Temp. Sensor)  SI. No : BAS-H2DF-30  Range : 0 to 100° C  AHU No : 36 |  |  |
| **Reference No** | PRT:9147/2021-2022 |
| **Date of Calibration** | 13.09.2021 |
| **Recommended Due Date** | 12.09.2022 |
| **Environmental condition** | Temperature : 0 -100 0 C |
| Relative Humidity : 30-90% |
| **Instrument Condition** | Good |

|  |  |
| --- | --- |
| **Standard / Calibration Used** | **Traceable to** |
| TESTO 625 Thermo hygrometer  Sl.No:62936315 | Trace able to National Standards  Cert No: 012101349  Due Date: 02.08.2022 |

The Calibration used is traceable to national standards

**CALIBRATION RESULTS**

**TEMPERATURE**

|  |  |  |  |  |
| --- | --- | --- | --- | --- |
| **SL.No** | **Standard Readings** | **UUC Readings** | **Deviation** | **Max Error** |
| 1 | 15.2 | 15.0 | -0.2 | ±0.3°C |
| 2 | 25.1 | 25.2 | +0.1 | ±0.3°C |
| 3 | 35.3 | 35.6 | +0.3 | ±0.3°C |
| 4 | 57.2 | 57.1 | -0.1 | ±0.3°C |
| 5 | 97.2 | 97.5 | +0.3 | ±0.3°C |

**Remarks**: *All Parameters are well within the acceptable*

Calibrated by

Date: 13.09.2021

|  |  |  |  |
| --- | --- | --- | --- |
|  |  |  |  |
|  | |

**CALIBRATION CERTIFICATE**

|  |  |  |
| --- | --- | --- |
| **CUSTOMER NAME & ADDRESS:**  **M/s. Glenmark Pharmaceuticals Ltd.**  Plot No:-E37 To E39, D Road, MIDC Satpur, Nashik,  Maharashtra- 422007 |  |  |
|  |  |
|  |  |
|  |  |
| **INSTRUMENT DESCRIPTION**  Make : Protech Temperature Sensor  Model : AX-3(Fresh Air Temp. Sensor)  SI. No : BAS-H2DF-30  Range : 0 to 100° C  AHU No : 36 |  |  |
| **Reference No** | PRT:9148/2021-2022 |
| **Date of Calibration** | 13.09.2021 |
| **Recommended Due Date** | 12.09.2022 |
| **Environmental condition** | Temperature : 0 -100 0 C |
| Relative Humidity : 30-90% |
| **Instrument Condition** | Good |

|  |  |
| --- | --- |
| **Standard / Calibration Used** | **Traceable to** |
| TESTO 625 Thermo hygrometer  Sl.No:62936315 | Trace able to National Standards  Cert No: 012101349  Due Date: 02.08.2022 |

The Calibration used is traceable to national standards

**CALIBRATION RESULTS**

**TEMPERATURE (°C)**

|  |  |  |  |  |
| --- | --- | --- | --- | --- |
| **SL.No** | **Standard Readings** | **UUC Readings** | **Deviation** | **Max Error** |
| 1 | 15.2 | 14.9 | -0.3 | ±0.3°C |
| 2 | 25.1 | 25.3 | +0.2 | ±0.3°C |
| 3 | 35.3 | 35.0 | -0.3 | ±0.3°C |
| 4 | 57.2 | 57.3 | +0.1 | ±0.3°C |
| 5 | 97.2 | 97.4 | +0.2 | ±0.3°C |

**Remarks**: *All Parameters are well within the acceptable*

Calibrated by

Date: 13.09.2021

|  |  |  |  |
| --- | --- | --- | --- |
|  |  |  |  |
|  | |

**CALIBRATION CERTIFICATE**

|  |  |  |
| --- | --- | --- |
| **CUSTOMER NAME & ADDRESS:**  **M/s. Glenmark Pharmaceuticals Ltd.**  Plot No:-E37 To E39, D Road, MIDC Satpur, Nashik,  Maharashtra- 422007 |  |  |
|  |  |
|  |  |
|  |  |
| **INSTRUMENT DESCRIPTION**  Make : Protech Temperature Sensor  Model : AX-3(Coil 1. Sensor)  SI. No : BAS-H2DF-30  Range : 0 to 100° C  AHU No : 36 |  |  |
| **Reference No** | PRT:9149/2021-2022 |
| **Date of Calibration** | 13.09.2021 |
| **Recommended Due Date** | 12.09.2022 |
| **Environmental condition** | Temperature : 0 -100 0 C |
| Relative Humidity : 30-90% |
| **Instrument Condition** | Good |

|  |  |
| --- | --- |
| **Standard / Calibration Used** | **Traceable to** |
| TESTO 625 Thermo hygrometer  Sl.No:62936315 | Trace able to National Standards  Cert No: 012101349  Due Date: 02.08.2022 |

The Calibration used is traceable to national standards

**CALIBRATION RESULTS**

**TEMPERATURE (°C)**

|  |  |  |  |  |
| --- | --- | --- | --- | --- |
| **SL.No** | **Standard Readings** | **UUC Readings** | **Deviation** | **Max Error** |
| 1 | 05.2 | 04.9 | -0.3 | ±0.3°C |
| 2 | 10.1 | 10.2 | +0.1 | ±0.3°C |
| 3 | 15.3 | 15.2 | -0.1 | ±0.3°C |
| 4 | 27.2 | 27.0 | -0.2 | ±0.3°C |
| 5 | 47.2 | 47.4 | +0.2 | ±0.3°C |

**Remarks**: *All Parameters are well within the acceptable*

Calibrated by

Date: 13.09.2021

|  |  |  |  |
| --- | --- | --- | --- |
|  |  |  |  |
|  | |

**CALIBRATION CERTIFICATE**

|  |  |  |
| --- | --- | --- |
| **CUSTOMER NAME & ADDRESS:**  **M/s. Glenmark Pharmaceuticals Ltd.**  Plot No:-E37 To E39, D Road, MIDC Satpur, Nashik,  Maharashtra- 422007 |  |  |
|  |  |
|  |  |
|  |  |
| **INSTRUMENT DESCRIPTION**  Make : Protech Temperature Sensor  Model : AX-3(Coil 2. Sensor)  SI. No : BAS-H2DF-30  Range : 0 to 100° C  AHU No : 36 |  |  |
| **Reference No** | PRT:9150/2021-2022 |
| **Date of Calibration** | 13.09.2021 |
| **Recommended Due Date** | 12.09.2022 |
| **Environmental condition** | Temperature : 0 -100 0 C |
| Relative Humidity : 30-90% |
| **Instrument Condition** | Good |

|  |  |
| --- | --- |
| **Standard / Calibration Used** | **Traceable to** |
| TESTO 625 Thermo hygrometer  Sl.No:62936315 | Trace able to National Standards  Cert No: 012101349  Due Date: 02.08.2022 |

The Calibration used is traceable to national standards

**CALIBRATION RESULTS**

**TEMPERATURE (°C)**

|  |  |  |  |  |
| --- | --- | --- | --- | --- |
| **SL.No** | **Standard Readings** | **UUC Readings** | **Deviation** | **Max Error** |
| 1 | 05.2 | 05.1 | -0.1 | ±0.3°C |
| 2 | 10.1 | 10.2 | +0.1 | ±0.3°C |
| 3 | 15.3 | 15.1 | -0.2 | ±0.3°C |
| 4 | 27.2 | 27.0 | -0.2 | ±0.3°C |
| 5 | 47.2 | 47.4 | +0.2 | ±0.3°C |

**Remarks**: *All Parameters are well within the acceptable*

Calibrated by

Date: 13.09.2021