## COMPRESSOR
METER NAME: COMPRESSOR
METER TYPE: 0022
MODEL:
S.NO | PARAMETER | UNITS | M.F | NO.OF DIGITS | DATA TYPE
1 | KWH | Kwh | 1 | 8 | HEX
2 | KW | W | 0.001 | 8 | HEX
3 | KVAH | Kvh | 1 | 8 | HEX
4 | RUN HR UTILITY | Min | 59 | 8 | HEX
5 | TANK PRESSURE | Psi | 0.0606 | 4 | ASCII
6 | FILTER PRESSURE | Pa | 0.015 | 5 | ASCII
7 | TEMPERATURE | C | 1 | 6 | ASCII
8 | HUMIDITY | Per | 0.1 | 3 | ASCII
9 | FLOW RATE | Cu.M/hr | 1 | 4 | ASCII
10 | FLOW TOTAL | Cu.M | 1 | 10 | ASCII
11 | LOAD RHT | Min | 1 | 10 | ASCII
12 | NO LOAD RHT | Min | 1 | 10 | ASCII

## RESTROOM
METER NAME: RESTROOM MONITOR
METER TYPE: 0019
MODEL:
S.NO | PARAMETER | UNITS | M.F | NO.OF DIGITS | DATA TYPE
1 | NH3 MALE | % | 1 | 4 | ASCII
2 | NH3 FEMALE | % | 1 | 4 | ASCII
3 | MALE COUNT | cnt | 1 | 6 | ASCII
4 | FEMALE COUNT | cnt | 1 | 6 | ASCII
5 | WATER LEVEL | ltr | Depending on size of tank | 4 | ASCII
6 | FB GOOD COUNT | cnt | 1 | 4 | ASCII
7 | FB AVRG COUNT | cnt | 1 | 4 | ASCII
8 | FB POOR COUNT | cnt | 1 | 4 | ASCII
9 | RFID 1 | cnt | 1 | 4 | ASCII
10 | RFID 2 | cnt | 1 | 4 | ASCII
11 | RFID 3 | cnt | 1 | 4 | ASCII
12 | RFID N | cnt | 1 | 4 | ASCII

## MODI REST ROOM
METER NAME: RESTROOM MONITOR (MODIFIED)
METER TYPE: 0019
MODEL:
S.NO | PARAMETER | UNITS | M.F | NO.OF DIGITS | DATA TYPE
1 | NH3 - 1
2 | NH3 - 2
3 | MALE COUNT
4 | FEMALE COUNT
5 | WATER LEVEL
6 | FB GOOD COUNT
7 | FB AVRG COUNT
8 | FB POOR COUNT
9 | NH3 - 3
10 | NH3 - 4
11 | RFID 1
12 | RFID 2
13 | RFID 3
14 | RFID N

## COLD STG
METER NAME: COLD STORAGE MONITOR
METER TYPE: 0020
MODEL:
S.NO | PARAMETER | UNITS | M.F | NO.OF DIGITS | DATA TYPE
1 | TEMP CH-1 | °C | 1 | 6 | ASCII
2 | TEMP CH-2 | °C | 1 | 6 | ASCII
3 | DOOR1 COUNTER | cnt | 1 | 6 | ASCII
4 | DOOR2 COUNTER | cnt | 1 | 6 | ASCII
5 | DOOR1 TIMER | min | 1 | 6 | ASCII
6 | DOOR2 TIMER | min | 1 | 6 | ASCII

## TEMPERATURE
METER NAME: TEMPERATURE
METER TYPE: 0003
MODEL:
S.NO | PARAMETER | UNITS | M.F | NO.OF DIGITS | DATA TYPE
1 | TEMP CH-1 | °C | 1 | 6 | ASCII
2 | TEMP CH-2 | °C | 1 | 6 | ASCII
3 | TEMP CH-3 | °C | 1 | 6 | ASCII
4 | TEMP CH-4 | °C | 1 | 6 | ASCII
5 | TEMP CH-5 | °C | 1 | 6 | ASCII
6 | TEMP CH-6 | °C | 1 | 6 | ASCII
7 | TEMP CH-7 | °C | 1 | 6 | ASCII
8 | TEMP CH-8 | °C | 1 | 6 | ASCII
9 | TEMP CH-9 | °C | 1 | 6 | ASCII
10 | TEMP CH-10 | °C | 1 | 6 | ASCII

## FUEL
METER NAME: FUEL
METER TYPE: 0004
MODEL:
S.NO | PARAMETER | UNITS | M.F | NO.OF DIGITS | DATA TYPE
1 | FUEL LEVEL | ltr | 1
2 | FUEL TOTALIZER | ltr | 1
3 | CONSUMPTION TOTALS | ltr | 1

## FUEL1
METER NAME: FUEL 1
METER TYPE: 0008
MODEL:
S.NO | PARAMETER | UNITS | M.F | NO.OF DIGITS | DATA TYPE
1 | FUEL LEVEL | ltr | 1 | 10 | ASCII
2 | FUEL TOTALIZER | ltr | 1 | 10 | ASCII
3 | CONSUMPTION TOTALS | ltr | 1 | 10 | ASCII
4 | DG RUNNING TIME(MIN) | min | 1 | 10 | ASCII
5 | DG STATUS | 0 (off)/1 (on) |  | 1 | ASCII
6 | BAT VOLT | volts | 1 | 6 | ASCII

## FUEL SENSOR
METER NAME: FUEL SENSOR
METER TYPE:
MODEL:
S.NO | PARAMETER | UNITS | M.F | NO.OF DIGITS | DATA TYPE
1 | Fuel Level | LTR | 1 | 10 | ASCII
2 | Fuel Totalizer | LTR | 1 | 10 | ASCII
3 | Consume Tot | LTR | 1 | 10 | ASCII
4 | RHT | MIN | 1 | 10 | ASCII
5 | DG Status | 0/1 | 1 | 1 | ASCII
6 | BatteryVolt | VOLTS | 1 | 6 | ASCII
7 | Oil Pressure | 0/1 | 1 | 1 | ASCII
8 | Coolant Alarm | 0/1 | 1 | 1 | ASCII

## MCB
METER NAME: MCB
METER TYPE: 0021
MODEL:
S.NO | PARAMETER | UNITS | M.F | NO.OF DIGITS | DATA TYPE
1 | PHASE-1 CURRENT
2 | PHASE-2 CURRENT
3 | PHASE-3 CURRENT
4 | NEUTERAL CURRENT
5 | 1-N VOLTAGE
6 | 2-N VOLTAGE
7 | 3-N VOLTAGE
8 | 1-2 VOLTAGE
9 | 1-3 VOLTAGE
10 | 2-3 VOLTAGE
11 | PHASE-1 THD CURRENT
12 | PHASE-2 THD CURRENT
13 | PHASE-3 THD CURRENT
14 | NEUTRAL THD CURRENT
15 | 1-N THD VOLTAGE
16 | 2-N THD VOLTAGE
17 | 3-N THD VOLTAGE
18 | 3 PHASE ACTIVE POWER
19 | 3 PHASE REACTIVE POWER
20 | 3 PHASE POWER FACTOR
21 | 3 PHASE FREQUENCY
22 | +VE 3 PHASE ACTIVE ENERGY
23 | -VE 3 PHASE ACTIVE ENERGY
24 | +VE 3 PHASE REACTIVE ENERGY
25 | -VE 3 PHASE REACTIVE ENERGY
26 | SENSOR 1 TEMP VALUE
27 | BREAKER OPEN
28 | BREAKER CLOSED
29 | BREAKER TRIPPED

## ENVIRONMENT
METER NAME: ENVIRONMENT
METER TYPE: 0023
MODEL:
S.NO | PARAMETER | UNITS | M.F | NO.OF DIGITS | DATA TYPE
1 | TEMP | c | 1 | 6 | ASCII
2 | HUMIDITY | per | 0.1 | 3 | ASCII
3 | PRESSURE | pa | 0.1666 | 5 | ASCII

## MECHANICAL COUNTER
METER NAME: MECHANICAL COUNTER
METER TYPE: 0024
MODEL:
S.NO | PARAMETER | UNITS | M.F | NO.OF DIGITS | DATA TYPE
1 | COUNTER | ltr | 1

## WATER LEVEL
METER NAME: WATER LEVEL
METER TYPE: 0012
MODEL:
S.NO | PARAMETER | UNITS | M.F | NO.OF DIGITS | DATA TYPE
1 | LEVEL 1 | ltr | depending on size of tank | 4 | ASCII
2 | LEVEL 2 | ltr | depending on size of tank | 4 | ASCII
3 | LEVEL 3 | ltr | depending on size of tank | 4 | ASCII
4 | LEVEL 1 - FT | ltr | depending on size of tank | 10 | ASCII
5 | LEVEL 1 - CFT | ltr | depending on size of tank | 10 | ASCII

## AIR BALANCER
METER NAME: AIR BALANCER
METER TYPE: 0025
MODEL:
S.NO | PARAMETER | UNITS | M.F | NO.OF DIGITS | DATA TYPE
1 | PRESSURE | pa | 0.01
2 | DAC COUNT | cnt | 1
3 | SENSOR COUNT | cnt | 1

## MEDICAL GAS
METER NAME: MEDICAL GAS
METER TYPE: 0028
MODEL:
S.NO | PARAMETER | UNITS | M.F | NO.OF DIGITS | DATA TYPE
1 | FLOW TOTALS | kgs | 0.61505 | 11 | ASCII

## MUNTER & AC
METER NAME:MUNTER AND AC CONTROLLER
METER TYPE:0029
MODEL:
S.NO | PARAMETER | UNITS | M.F | NO OF DIGITS | DATA TYPE
1 | TEMPERATURE | °C | 1 | 6 | ASCII
2 | HUMIDITY | % | 0.1 | 3 | ASCII
3 | UNIT RUN STATUS | 0 (off)/1 (on) | 1 | 1 | ASCII
4 | AC RUN STATUS | 0 (off)/1 (on) | 1 | 1 | ASCII
5 | MUNTER RUN STATUS | 0 (off)/1 (on) | 1 | 1 | ASCII

## HVAC
METER NAME: HVAC
METER TYPE: 0017
MODEL:
S.NO | PARAMETER | UNITS | M.F | NO.OF DIGITS | DATA TYPE
1 | RETURN AIR TEMP | °C | 1 | 6 | ASCII
2 | UNIT STATUS | 0 (off)/1 (on) | 1 | 1 | ASCII
3 | COMPRESSOR STATUS | 0 (off)/1 (on) | 1 | 1 | ASCII
4 | UNIT RHT | minutes | 1 | 10 | ASCII
5 | COMPRESSOR RHT | minutes | 1 | 10 | ASCII
6 | FILTER PRESSURE | Pa | 0.1666 | 5 | ASCII
7 | SUPPLY AIR TEMP | °C | 1 | 6 | ASCII
8 | MANUAL MODE COUNTER | count | 1 | 5 | ASCII
9 | SET TEMP | °C | 1 | 6 | ASCII
10 | DELTA T | °C | 0.1 | 5 | ASCII
11 | CHWS TEMP | °C | 1 | 6 | ASCII
12 | CHWR TEMP | °C | 1 | 6 | ASCII
13 | ACTUATOR LEVEL | % | 0.3921 | 3 | ASCII

## EM SCHNEIDER 6438
METER NAME: SCHNEIDER EM
METER TYPE: 0002
MODEL: 6438 (DUAL)
S.NO | PARAMETER | UNITS | M.F | NO.OF DIGITS | DATA TYPE
1 | DG_KWH | W | 0.001 | 8 | HEX
2 | DG_KW | W | 0.001 | 8 | HEX
3 | EB_KWH | W | 0.001 | 8 | HEX
4 | EB_KW | W | 0.001 | 8 | HEX

## EM SCHNEIDER 64XX
METER NAME: SCHNEIDER ENERGY METER
METER TYPE: 0002
MODEL: 64XX SERIES
S.NO | PARAMETER | UNITS | M.F | NO.OF DIGITS | DATA TYPE
1 | DG_KWH | W | 0.001 | 8 | HEX
2 | DG_KW | W | 0.001 | 8 | HEX
3 | EB_KWH | W | 0.001 | 8 | HEX
4 | EB_KW | W | 0.001 | 8 | HEX
5 | PF |  | 1 | 8 | HEX
6 | KVA | VA | 0.001 | 8 | HEX
7 | DG_RUN HOUR |  |  | 8 | HEX
8 | EB_KVAH | VAH | 0.001 | 8 | HEX
9 | DG_KVAH | VAH | 0.001 | 8 | HEX
10 | CURRENT-1 | A | 1 | 8 | HEX
11 | CURRENT-2 | A | 1 | 8 | HEX
12 | CURRENT-3 | A | 1 | 8 | HEX
13 | VOLTAGE-1 | V | 1 | 8 | HEX
14 | VOLTAGE-2 | V | 1 | 8 | HEX
15 | VOLTAGE-3 | V | 1 | 8 | HEX

## EM SCHNEIDER 1130
METER NAME: SCHNEIDER EM
METER TYPE: 0002
MODEL: 1130H
S.NO | PARAMETER | UNITS | M.F | NO.OF DIGITS | DATA TYPE
1 | KWH (GEN) | kwh | 1 | 8 | HEX
2 | KW (GEN) | kw | 1 | 8 | HEX
3 | KWH (EB) | kwh | 1 | 8 | HEX
4 | KW (EB) | kw | 1 | 8 | HEX
5 | PF AVG |  | 1 | 8 | HEX
6 | KVA | VA | 0.001 | 8 | HEX
7 | RUN HOUR (GEN) |  |  | 8 | HEX
8 | KVAH (EB) | VAH | 0.001 | 8 | HEX
9 | KVAH (GEN) | VAH | 0.001 | 8 | HEX
10 | CURRENT-1 | A | 1 | 8 | HEX
11 | CURRENT-2 | A | 1 | 8 | HEX
12 | CURRENT-3 | A | 1 | 8 | HEX
13 | VOLTAGE-1 | V | 1 | 8 | HEX
14 | VOLTAGE-2 | V | 1 | 8 | HEX
15 | VOLTAGE-3 | V | 1 | 8 | HEX

## EM RISHABH 2340
METER NAME: RISHABH EM
METER TYPE: 0002
MODEL: 23-13 SERIES
S.NO | PARAMETER | UNITS | M.F | NO.OF DIGITS | DATA TYPE
1 | DG_KWH | KWH | 1 | 8 | HEX
2 | DG_KW | W | 0.001 | 8 | HEX
3 | EB_KWH | KWH | 1 | 8 | HEX
4 | EB_KW | W | 0.001 | 8 | HEX
5 | PF |  | 1 | 8 | HEX
6 | EB_KVA | VA | 0.001 | 8 | HEX
7 | DG_RUN HOUR | MIN |  | 8 | HEX
8 | EB_KVAH | KVAH | 1 | 8 | HEX
9 | DG_KVAH | KVAH | 1 | 8 | HEX
10 | CURRENT-1 | A | 1 | 8 | HEX
11 | CURRENT-2 | A | 1 | 8 | HEX
12 | CURRENT-3 | A | 1 | 8 | HEX
13 | VOLTAGE-1 | V | 1 | 8 | HEX
14 | VOLTAGE-2 | V | 1 | 8 | HEX
15 | VOLTAGE-3 | V | 1 | 8 | HEX
16 | VA SUM | VA | 0.001 | 8 | HEX
17 | VAR SUM | VA | 0.001 | 8 | HEX
18 | VARH SUM | VAH | 1 | 8 | HEX
19 | VOLT 1-2 | V | 1 | 8 | HEX
20 | VOLT 2-3 | V | 1 | 8 | HEX
21 | VOLT 1-3 | V | 1 | 8 | HEX
22 | FREQ | HZ | 1 | 8 | HEX
23 | KVARH (LAG) | VAH | 1 | 8 | HEX
24 | VTHD R PHASE | % | 1 | 8 | HEX
25 | VTHD Y PHASE | % | 1 | 8 | HEX
26 | VTHD B PHASE | % | 1 | 8 | HEX

## DM 1200
METER NAME: DM EM
METER TYPE:0002
MODEL: 1200
S.NO | PARAMETER | UNITS | M.F | NO.OF DIGITS | DATA TYPE
1 | KWH | kwh | 0.001 | 8 | HEX
2 | KW | w | 0.001 | 8 | HEX

## TEMP AND PRE 0027
METER NAME: TEMP AND PRESSURE
METER TYPE: 0027
MODEL:
S.NO | PARAMETER | UNITS | M.F | NO.OF DIGITS | DATA TYPE
1 | TEMP 1
2 | TEMP 2
3 | TANK PRESSURE
4 | TANK PRESSURE

## Hydrent pressure
DUAL TEMPERATURE & PRESSURE
Meter Type 0027
Board Name:DUAL TEMPERATURE & PRESSURE 915Mhz & 868Mhz CommunicationTesting
Board Number:-PT0102V2 Starting add:-52 Max add:-179
Max Channel:32 Version:-1 DATE:05/12/2019
Total String:- |  | 26
S.NO | PARAMETER | NO.OF DIGITS | String Format
1 | Temperature1 | 6 | 26
2 | Temperature2 | 6 | 26
3 | Pressure1 | 4 | 3597
4 | Pressure2 | 4 | 3405

## 4 Ch Controller with feed back
4-CH SWITCH CONTROLLER WITH FEEDBACK
Board Name:4-CH SWITCH CONTROLLER WITH FEEDBACK 915Mhz & 868Mhz CommunicationTesting
Board Number:PT0106V2 Starting add:-1024 Max add:-1279
Max Channel:32 Version:-02 DATE:25/11/2019
Total String:- |  | 1
S.NO | PARAMETER | NO.OF DIGITS | String Format
1 | Switch 1/relay 1 | 6 | 1
2 | Switch 2/Relay 2 | 6 | 2
3 | Switch 3/Relay 3 | 6 | 4
4 | Switch 4/Relay 4 | 6 | 2
5 | Switch Status/Relay Status | 4 | 101
6 | FB1 | 1 | 0
7 | FB2 | 1 | 1
8 | FB3 | 1 | 0
9 | FB4 | 1 | 0
10 | TS1 | 1 | 1
11 | TS2 | 1 | 0
12 | TS3 | 1 | 1
13 | TS4 | 1 | 1

## WS01
TEMPERATURE & HUMIDITY & WIND SPEED
Meter Type WS01
S.NO | PARAMETER | NO.OF DIGITS | String Format
1 | Temperature1 | 6 | 26
2 | RH Humidity | 3 | 359
3 | Wind Speed | 4 | 3590

## AMC01
AHU MONITOR
Meter Type AM01
S.NO | PARAMETER | NO.OF DIGITS | DATA TYPE
1 | Temperature T1 | 5 | 26
2 | Temperature T2 | 5 | 26
3 | Temperature T3 | 5 | 26
4 | Temperature T4 | 5 | 26
5 | Temperature T5 | 5 | 26
6 | Temperature T6 | 5 | 26
7 | Temperature T7 | 5 | 26
8 | Temperature T8 | 5 | 26
9 | Delta T2-T1 | 5 | 5195 | ΔT Fresh Air | T1 freash air Temperature After HRW
10 | Delta T4-T3 | 5 | 5195 | ΔT Exhaust Air | T2 freash air Temperature
11 | Filter Pressure | 5 | 6890 |  | T3 Return Air Temperature
T4 Exhaust Air Temperature After HRW
T5 Supply Air Temperature

## GB01
Gas Bank Controller
Meter Type GB01
S.NO | PARAMETER | NO.OF DIGITS | DATA TYPE
1 | Gas Pressure 1 | 3 | 12
2 | Gas Pressure 2 | 3 | 12
3 | Set Pressure | 2 | 20
4 | Set Timer | 2 | 10
5 | Gas bank 1 status | 1 | 1 or 0
6 | Gas bank 2 status | 1 | 1 or 0
7 | Solonide 1 Status | 1 | 1 or 0
8 | Solonide 2 Status | 1 | 1 or 0

## HD07
Glenmark Map Memory Map
HD07
S.NO | PARAMETER | NO.OF DIGITS
1 | UNIT STATUS | 1
2 | RA TEMP | 5
3 | RA HUMIDITY | 3
4 | RA DEW POINT TEMP | 4
5 | SA TEMP | 5
6 | SA HUMIDITY | 3
7 | SA DEW POINT TEMP | 4
8 | RA SET TEMP | 4
9 | SA SET TEMP | 4
10 | DELTA T AIR | 5
11 | CHWS TEMP | 5
12 | CHWR TEMP | 5
13 | DELTA T CW | 5
14 | UNIT RHT | 7
15 | PREFILTER PRESSURE | 5
16 | FINE FILTER PRESSURE | 5
17 | DUCT PRESSURE | 5
18 | DUCT SET PRESSURE | 3
19 | AIR VELOCITY | 4
20 | AIR VEL. SET VALUE | 4
21 | CW ACTUATOR O/P or CW Actuator Level | 3 | 255(100% OPEN) *0.3921
22 | CW ACTUATOR F/B | 3
23 | HW ACTUATOR O/P | 3
24 | VFD O/P | 3
25 | MODE | 1

## Munter Auto control New
METER NAME:MUNTER AND AC CONTROLLER
METER TYPE:0029
MODEL:
S.NO | PARAMETER | UNITS | M.F | NO OF DIGITS | DATA TYPE
1 | TEMPERATURE | °C | 1 | 6 | ASCII
2 | HUMIDITY | % | 0.1 | 3 | ASCII
3 | UNIT RUN STATUS | 0 (off)/1 (on) | 1 | 1 | ASCII
4 | AC RUN STATUS | 0 (off)/1 (on) | 1 | 1 | ASCII
5 | MUNTER RUN STATUS | 0 (off)/1 (on) | 1 | 1 | ASCII
METER NAME:MUNTER AC CONTROLLER
METER TYPE:MC01
MODEL:
S.NO | PARAMETER | UNITS | M.F | NO OF DIGITS | DATA TYPE
1 | TEMPERATURE | °C | 1 | 5 | ASCII
2 | SET TEMPERATURE | °C |  | 4 | ASCII
3 | HUMIDITY | % | 0.1 | 3 | ASCII
4 | SET HUMIDITY | % | 0.1 | 3 | ASCII
5 | UNIT RUN STATUS | 0 (off)/1 (on) | 1 | 1 | ASCII
6 | AC RUN STATUS | 0 (off)/1 (on) | 1 | 1 | ASCII
7 | MUNTER RUN STATUS | 0 (off)/1 (on) | 1 | 1 | ASCII
8 | AC RUNTIME |  |  | 7 | ASCII
9 | MUNTER RUNTIME |  |  | 7 | ASCII

## Status Monitor
Status Monitor (ST01)
S.NO | PARAMETER | NO.OF DIGITS
1 | Stauts 1 | 1
2 | Stauts 2 | 1
3 | Stauts 3 | 1
4 | Stauts 4 | 1
5 | Stauts 5 | 1
6 | Stauts 6 | 1
7 | Stauts 7 | 1
8 | Stauts 8 | 1
9 | Unit Runtime 1 | 6
10 | Unit Runtime 2 | 6
11 | Unit Runtime 3 | 6
12 | Unit Runtime 4 | 6
13 | Unit Runtime 5 | 6
14 | Unit Runtime 6 | 6
15 | Unit Runtime 7 | 6
16 | Unit Runtime 8 | 6

## Cold Room Independent CR01
METER NAME: COLDROOM INDEPENDENT(CR01)
METER TYPE: CR01
MODEL:
S.NO | PARAMETER | UNITS | M.F | NO.OF DIGITS | DATA TYPE
1 | TEMP 1 | °C | 1 | 5 | ASCII
2 | TEMP 2 |  |  | 5 | ASCII
3 | TEMP 3 |  |  | 5 | ASCII
4 | TEMP 4 |  |  | 5 | ASCII
5 | TEMP 5 |  |  | 5 | ASCII
6 | TEMP 6 |  |  | 5 | ASCII
7 | TEMP 7 |  |  | 5 | ASCII
8 | TEMP 8 |  |  | 5 | ASCII
9 | D1 COUNT |  |  | 6 | ASCII
10 | D2 COUNT |  |  | 6 | ASCII
11 | D1 RHT |  |  | 6 | ASCII
12 | D2 RHT |  |  | 6 | ASCII
13 | EM KWH |  |  | 8 | Hex
14 | EM KW |  |  | 8 | Hex
15 | EM PF |  |  | 8 | Hex
16 | EM CURRENT1 |  |  | 8 | Hex
17 | EM CURRENT2 |  |  | 8 | Hex
18 | EM CURRENT3 |  |  | 8 | Hex
19 | EM VOLTAGE1 |  |  | 8 | Hex
20 | EM VOLTAGE2 |  |  | 8 | Hex
21 | EM VOLTAGE3 |  |  | 8 | Hex